Division 28 16 00– Electric Safety and Security

- Intrusion detection -

# 

# 

# The intrusion alarm system shall be in accordance with EN 50131-3 for surveillance of medium-to-large projects.

* The system shall be easily extensible up to 1016 devices by supporting addressable point bus technology.
* The system shall be a high security intrusion alarm system that makes use of fault-tolerant and redundant bus technology to continue even in case of failure.
* Automatic addressing and set up of the devices shall be possible.
* The system shall support an open, IP-based interface that allows for full access to and control of all parts of the system and the integration into a management system.

Table of Contents

[**PART 1** **GENERAL** 3](#_Toc448243807)

[1.01 Quality Assurance 3](#_Toc448243808)

[1.02 Certifications 3](#_Toc448243811)

[**PART 2** **PRODUCTS** 4](#_Toc448243813)

[2.01 General 4](#_Toc448243814)

[2.02 Control Panel 7](#_Toc448243820)

[2.03 Keypad 10](#_Toc448243828)

[2.04 Point Bus Extension Module 13](#_Toc448243835)

[2.05 Interface Module 15](#_Toc448243843)

[2.06 Optional CAN Bus Splitter Module 17](#_Toc448243850)

[2.07 Optional Expansion Module 18](#_Toc448243856)

[2.08 Optional Arming Device 18](#_Toc448243861)

[2.09 Panel Enclosure 19](#_Toc448243864)

[2.010 Optional Power Enclosure 19](#_Toc448243870)

[2.011 Optional Expansion Enclosure 20](#_Toc448243875)

[2.012 Power Supply 21](#_Toc448243879)

[2.013 Manufactured units 24](#_Toc448243885)

[**PART 3** **EXECUTION** 25](#_Toc448243899)

[3.01 Installation 25](#_Toc448243900)

[3.02 Training and Support 25](#_Toc448243904)

[**PART 4** **Other** 26](#_Toc448243906)

[4.01 Attachments (optional) 26](#_Toc448243907)

[4.02 Further applicable documents (optional) 26](#_Toc448243908)

[4.03 List of abbreviations (optional) 26](#_Toc448243909)

[4.04 Revision History 26](#_Toc448243910)

# **GENERAL**

## Quality Assurance

### Installation, programming and maintenance of the intrusion alarm system shall be performed by qualified installers fully trained by the manufacturer.

### Manufacturer’s warranty shall cover at least 3 years.

## Certifications

### The intrusion alarm system shall be featured to obtain the following certifications:

#### EN 50131–1 Grade 3

#### EN 50131–3

#### EN 50131–6

#### SES-EMA-RL-T2

#### VdS 2311 Class C

#### VdS 2344

#### VdS 2110

#### VdS 2469

#### VdS 2203

#### VdS 2115

#### VdS 2252

#### AFNOR – NF&A2P Grade 3

# **PRODUCTS**

## General

### The system shall be a scalable intrusion alarm system for medium to large applications and shall be equipped with and support the following features:

#### Certified for EN 50131-1 Grade 3, AFNOR – NF&A2P Grade 3, SES-EM-RL-T2 and VdS 2311 Class C.

#### Support up to 1016 devices by using addressable point bus technology.

#### Support up to 500 areas.

#### Support up to 996 users.

#### Support up to 1500 addresses.

#### Support up to 32 touch keypads, which can be operated in multiple languages (DE, EN, FR, NL, HU, PL, RU, IT, ES, CZ, PT, LV).

#### Equipped with an open, IP-based interface that allows for the following functions:

##### Integration into a management system.

##### Full access to and control of all parts of the system.

##### Fast and easy integration via state of the art web technologies (REST, JSON).

##### Customizable event notification mechanism for instant notification of alarms or state changes.

##### Direct connection to the interface of the panel without an extra server application needed in between.

#### Remote programming via Ethernet (RJ45) connection.

#### It shall be possible to upgrade the firmware of all devices of the intrusion alarm system via remote programming software.

#### Schedules that allow for automated arming and disarming.

### Wiring considerations for devices on the external bus:

#### 0.6 mm – 1.0 mm d, recommended 0.8 mm.

#### Solid or stranded.

#### Twisted or untwisted.

#### Shielded or unshielded.

#### Cable length up to 1000 m.

#### Each peripheral device has two sets of bus terminals for daisy chain in/out wiring.

#### Peripheral devices are grounded through the bus cable.

### Electrical

|  |  |
| --- | --- |
| Maximum operating voltage in VAC | 230 (-15%, +10%) |
| Minimum AC line frequency in Hz | 47 |
| Maximum AC line frequency in Hz | 63 |
| Maximum power consumption in W per power supply | 150 |
| Minimum battery capacity in Ah per power supply | 18 |
| Maximum battery capacity in Ah per power supply | 80 |
| Back-up time | Determined by battery capacity and system load. Consider time or capacity limits for recharging the batteries regarding local regulations or EN standards if needed. |

### Mechanical

|  |  |
| --- | --- |
| **Panel enclosure** |  |
| Dimension in cm (H x W x D) | 65.8 x 44.3 x 19.35 |
| Weight in g | 1566 |
| **Power enclosure** |  |
| Dimension in cm (H x W x D) | 65.8 x 44.3 x 19.35 |
| Weight in g | 1566 |
| **Expansion enclosure** |  |
| Dimension in cm (H x W x D) | 43.6 x 44.3 x 11.2 |
| Weight in g | 780 |
| **System parameters** |  |
| Number of addresses | 1500 |
| Number of areas | 500 |
| Number of users | 996 |
| Number of PINs | 996 (with 9 digits, supporting a  3-digit user ID (004 - 999) and a  6-digit passcode) |
| Number of possible combination per PINs | 1 million |
| Validity of PINs | Permanent validity, time-limited  validity or one-time use  configurable |
| **Number of devices** |  |
| Point bus extension modules | 8 |
| Keypads | 32 |
| Power supplies 150 W | 32 |
| Printers | 1 |
| CAN Bus splitter modules | 8 |
| **Number of inputs** |  |
| Programmable inputs on addressable point bus | Limited to maximum number of available addresses system wide |
| Number of inputs (on control panel) | 8 |
| **Number of outputs** |  |
| Programmable outputs on addressable point bus | Limited to maximum number of available addresses system wide |
| Power drive (on control panel) | 2 |
| Dry contact (on control panel) | 2 |
| Auxiliary power (on control panel) | 1 |
| Supervised output (on interface module) | 3 |
| Open-collector output (on interface module) | 2 |

### Environmental

|  |  |
| --- | --- |
| Minimum operating temperature in °C | -10 |
| Maximum operating temperature in °C | 55 |
| Minimum storage temperature in °C | -20 |
| Maximum storage temperature in °C | 60 |
| Minimum relative humidity in % | 5 |
| Maximum relative humidity in % | 95 |
| Protection class | IP30  IP31 (with an edge protection profile) |
| Security level | IK06 |
| Environmental class | II: EN60950-1 ; EN50130-4 ;  EN50131-1 ; VdS 2110 |
| Usage | Indoor |

## Control Panel

### The control panel shall support:

#### 1500 addresses.

#### 500 areas.

#### 996 users.

### The control panel shall be equipped with and support:

#### 8 supervised inputs and 1 unsupervised tamper input.

#### 2 programmable outputs for optical and acoustical signaling devices as well as for other local notification devices.

#### 2 programmable relay outputs and 1 auxiliary output.

#### 2 bus interfaces and 1 Ethernet port.

#### An open, IP-based interface that allows for the following functions:

##### Integration into a management system.

##### Full access to and control of all parts of the system.

##### Fast and easy integration via state of the art web technologies (REST, JSON).

##### Customizable event notification mechanism for instant notification of alarms or state changes.

##### Direct connection to the interface of the panel without an extra server application needed in between.

### Firmware Upgrades:

#### It shall be possible to upgrade the control panel via remote programming software.

### Electrical:

|  |  |
| --- | --- |
| Minimum operating voltage  in VDC | 19 |
| Maximum operating voltage in VDC | 29 |
| Rated voltage in VDC | 28 |
| Minimum current consumption in mA | 250 |
| Maximum current consumption in mA | 500 |
| **Outputs** |  |
| Maximum current consumption in mA per output | 1000 |
|  |  |
| **Relay outputs** |  |
| Maximum operating voltage in VDC | 30 |
| Maximum operating voltage in VAC | 30 |
| Back-up time | Determined by battery capacity and system load. Consider time or capacity limits for recharging the batteries regarding local regulations or EN standards if needed. |

### Mechanical:

|  |  |
| --- | --- |
| Dimension in cm (H x W x D) | 14.6 x 21.6 x 5.5 |
| Weight in g | 450 |
| Indicators | Green LED for operating status |
| **Number of output modules** |  |
| Auxiliary output | 1 |
| Power output | 2 |
| Form C dry-contact relay output | 2 |

### Environmental:

|  |  |
| --- | --- |
| Minimum operating temperature in °C | -10 |
| Maximum operating temperature in °C | 55 |
| Minimum storage temperature in °C | -20 |
| Maximum storage temperature in °C | 60 |
| Minimum relative humidity in % | 5 |
| Maximum relative humidity in % | 95 |
| Protection class | IP30  IP31 (built into the panel enclosure with an edge protection profile) |
| Security level | IK04  IK06 (built into the panel enclosure with an edge protection profile) |
| Environmental Class | II:  EN50130-5, VdS 2110 |
| Usage | Indoor |

## Keypad

### It shall be possible to connect up to 32 keypads to the system.

### The keypad shall support the following functions:

#### Touch screen – 14 cm LCD with adjustable LED backlight.

#### Graphic interface:

##### 16-bit vivid color.

##### 320 x 240 pixel resolution.

##### Intuitive icons and menus.

#### Built-in speaker with adjustable volume supporting the following audible tones:

##### Accepted button press tone.

##### Invalid tone.

##### Entry delay tone.

##### Exit delay tone.

##### Intrusion alarm tone.

##### Intrusion supervisory tone.

##### Intrusion trouble tone.

##### Chime tone.

##### System trouble tone.

#### Language option, individually selectable by user:

##### DE, EN, FR, NL, HU, PL, RU, IT, ES, CZ, PT, LV.

#### Arming/disarming either the whole system or a subset of the system.

#### If the system is not ready to arm, the keypad shall immediately show the cause.

#### User configuration:

##### Add user.

##### Delete user.

##### Edit user.

##### Change password.

#### Built-in tamper switch.

#### Terminal blocks and system connectors attached to the base.

#### The menu structure shall be adaptable to the authorizations of different users.

### Firmware Upgrades:

#### It shall be possible to upgrade the keypad via remote programming software.

### Electrical:

|  |  |
| --- | --- |
| Minimum operating voltage in VDC | 16 |
| Maximum operating voltage in VDC | 29 |
| Rated voltage in VDC | 28 |
| **Rated current in mA** |  |
| Start-up | 800 |
| Alarm | 175 |
| Idle screen | 100 |
| Dark idle screen | 60 |

### Mechanical:

|  |  |
| --- | --- |
| Dimension in cm (H x W x D) | 15.6 x 17.1 x 3.9 |
| Weight in g | 363 |
| Housing material | ABS plastic |
| Color | White textured |
| **Touchscreen** |  |
| Type | TFT-LCD |
| Diagonal in cm | 14 |
| Aspect ratio | 4:3 |
| Resolution in pixels | 320 x 240 |
| Color depth | 16-bit color |
| Backlight | White LED with adjustable brightness (active and idle) |
| Indicators | 3 LEDs:   * Green: Power * Yellow: Fault * Red: Alarm |
| Connection type | 4-wire bus, 2 sets of terminals for daisy chain in/out wiring |

### Environmental:

|  |  |
| --- | --- |
| Minimum operating temperature in °C | -10 |
| Maximum operating temperature in °C | 55 |
| Minimum storage temperature in °C | -20 |
| Maximum storage temperature in °C | 60 |
| Minimum relative humidity in % | 5 |
| Maximum relative humidity in % | 95 |
| Protection class | IP31 |
| Security level | IK06 |
| Design type as per EN 50131 | B |
| Environmental Class | II: EN50130-5, VdS 2110 |
| Usage | Indoor |

## Point Bus Extension Module

### The intrusion alarm system shall support up to 8 point bus extension modules.

### Each point bus extension module shall support the following functions:

#### Connect addressable point bus network with support of 1 loop or 2 stubs at maximum output current of 300 mA.

#### Support up to 127 addressable point bus network devices on either 1 loop or 2 stubs.

#### Support 2 auxiliary power outputs (500 mA each).

#### Provide single fault redundancy on loop configuration.

#### Provide automatic addressing and automatic set up.

### Firmware Upgrades:

#### It shall be possible to upgrade the point bus extension module via remote programming software.

### The point bus extension module shall support a range of:

#### Motion detectors.

#### Contacts.

#### Glassbreak detectors.

#### Seismic detectors.

#### Panic buttons.

#### Arming/Blocking devices.

#### Fire devices.

#### Sirens and LED lamps.

#### In/Out expansion modules to connect conventional devices to the system.

### Electrical:

|  |  |
| --- | --- |
| Minimum operating voltage in VDC | 16 |
| Maximum operating voltage in VDC | 29 |
| Rated voltage in VDC | 28 |
| Rated current in mA | 1600 |
| Standby current consumption | Dependent on addressable point bus network device load |
| Maximum addressable point bus network AUX output current in mA | 2 x 500 |

### Mechanical:

|  |  |
| --- | --- |
| Dimension in cm (H x W x D) | 15.88 x 8.26 x 6.35 |
| Weight in g | 365 |
| Housing material | ABS plastic |
| Color | Off-white |

### Environmental:

|  |  |
| --- | --- |
| Minimum operating temperature in °C | -10 |
| Maximum operating temperature in °C | 55 |
| Minimum storage temperature in °C | -20 |
| Maximum storage temperature in °C | 60 |
| Minimum relative humidity in % | 5 (non-condensing) |
| Maximum relative humidity in % | 95 (non-condensing) |
| Protection class | IP30  IP31 (built into the panel enclosure with an edge protection profile) |
| Security level | IK04  IK06 (built into the panel enclosure with an edge protection profile) |
| Environmental Class | II:  EN50130-5, VdS 2110 |
| Usage | Indoor |

## Interface Module

### The intruder alarm system shall support 1 interface module, which is the primary communication interface between the control panel and the communicator.

### The interface module shall support:

#### RS-232 COM 1 port: Interface to wireless GSM module or teleservice interface.

#### RS-232 COM 2 port: Shared with the 20 mA current loop on the terminal strip that supports connection to 1 printer through a 6-position terminal block.

#### 3 polarity-reversing supervised (12.1 kΩ EOL resistor) programmable outputs.

#### 2 unsupervised and programmable open-collector outputs.

### Firmware upgrades:

#### It shall be possible to upgrade the interface module via remote programming software.

### Electrical:

|  |  |
| --- | --- |
| Minimum operating voltage in VDC | 16 |
| Maximum operating voltage in VDC | 29 |
| Rated voltage in VDC | 28 |
| Minimum current consumption in mA | 100 |
| Maximum current consumption in mA | 150 |
| Outputs | * Unsupervised and programmable open-collector outputs able to sink up to a combined current of 0.5 A at  28 VDC. * Supervised and programmable outputs rated at 1 A each. |

### Mechanical:

|  |  |
| --- | --- |
| Dimension in cm (H x W x D) | 14.6 x 15.9 x 7.6 |
| Weight in g | 440 |
| Indicator | Green LED for device status |
| **Number of output modules** |  |
| Unsupervised and programmable open-collector | 2 |
| Supervised and programmable outputs rated | 3 |

### Environmental:

|  |  |
| --- | --- |
| Minimum operating temperature in °C | -10 |
| Maximum operating temperature in °C | 55 |
| Minimum storage temperature in °C | -20 |
| Maximum storage temperature in °C | 60 |
| Minimum relative humidity in % | 5 (non-condensing) |
| Maximum relative humidity in % | 95 (non-condensing) |
| Protection class | IP30  IP31 (built into the panel enclosure with an edge protection profile) |
| Enclosure Protection | IK04  IK06 (built into the panel enclosure with an edge protection profile) |
| Environmental Class | II:  EN50130-5, VdS 2110 |
| Usage | Indoor |

## Optional CAN Bus Splitter Module

### It shall be possible to connect up to 8 CAN Bus splitter modules to the system to enable flexible wiring into different directions.

### The installation of each CAN Bus splitter module shall enable 2 independent and isolated stubs to connect keypads, point bus extension modules and power supplies to the system.

### The maximum wire length for each stub shall be 500 m.

### Electrical:

|  |  |
| --- | --- |
| Minimum operating voltage in VDC | 16 |
| Maximum operating voltage in VDC | 29 |
| Rated voltage in VDC | 28 |
| Rated current in mA | 50 |
| Maximum output current in mA per stub | 900 |

### Mechanical:

|  |  |
| --- | --- |
| Dimensions in cm (H x W x D) | 15.9 x 8.3 x 6.4 |
| Weight in g | 168 |
| Housing material | ABS plastic |
| Color | Off-white |

### Environmental:

|  |  |
| --- | --- |
| Minimum operating temperature in °C | -10 |
| Maximum operating temperature in °C | 55 |
| Minimum storage temperature in °C | -20 |
| Maximum storage temperature in °C | 60 |
| Minimum relative humidity in % | 5 |
| Maximum relative humidity in % | 95 |
| Protection class | IP30 |
| Security level | IK04 |
| Environmental Class | II |

## Optional Expansion Module

### The optional expansion module shall provide the possibility to connect additional conventional devices to the system.

### The usage of expansion modules is limited by power consumption and the maximal amount of addresses.

### The expansion module shall support the following functions:

#### Connect 6 detector zones (conventional detector or monitoring contact inputs).

#### Connect 4 free control outputs.

#### Connect arming devices with associated system components.

#### Monitor the primary lines for alarms, short circuits or wire interruptions.

### An optional wall tamper contact shall be available.

## Optional Arming Device

### It shall be possible to arm/disarm the system via code keypad/reader or code keypad.

### The control unit of the arming device shall support the following elements:

#### Blocking element in combination with magnetic contact.

#### Bolt contact for monitoring perimeter door closed and locked.

#### Smart key.

#### Code keypad with integrated reader or as autonomous code keypad.

#### Reader.

#### Door opener relay or blocking element for vault doors.

## Panel Enclosure

### The panel enclosure shall be certified for VdS-S, EN and AFNOR.

### The panel enclosure shall be suitable for: 1 control panel, 1 interface module, 1 power supply, 2 x 40 Ah batteries and 4 point bus extension modules.

### The control panel enclosure shall be equipped with:

#### A hinged and removable mounting plate.

#### A removable cover.

#### Pre-configured cables.

#### A cable funnel.

### Mechanical:

|  |  |
| --- | --- |
| Dimension in cm (H x W x D) | 65.8 x 44.3 x 19.35 |
| Weight in g | 1566 |
| Material | 1.5 mm cold rolled steel |
| Color | White |

### Environmental:

|  |  |
| --- | --- |
| Protection class | IP30  IP31 (with an edge protection profile) |
| Security level | IK06 |
| Environmental class | II:  EN50130-5, VdS 2110 |
| Usage | Indoor |

## Optional Power Enclosure

### It shall be possible to add an optional power enclosure to the panel enclosure to increase the back-up time.

### The optional power enclosure shall be suitable for 1 power supply and 4 x 40 Ah batteries.

### Mechanical:

|  |  |
| --- | --- |
| Dimensions in cm (H x W x D) | 65.8 x 44.3 x 19.35 |
| Weight in g | 1566 |
| Material | 1.5 mm cold rolled steel |
| Color | White |

### Environmental:

|  |  |
| --- | --- |
| Protection class | IP30 |
| Security level | IK06 |
| Environmental class | II:  EN50130-5, VdS 2110 |
| Usage | Indoor |

## Optional Expansion Enclosure

### An optional expansion enclosure shall be suitable for 1 power supply and up to 2 x 18 Ah batteries or 4 point bus extension modules.

### Mechanical:

|  |  |
| --- | --- |
| Dimension in cm (H x W x D) | 43.6 x 44.3 x 11.2 |
| Weight in g | 780 |
| Material | 1.5 mm cold rolled steel |
| Color | White |

### Environmental:

|  |  |
| --- | --- |
| Protection class | IP30 |
| Security level | IK06 |
| Environmental class | II:  EN50130-5, VdS 2110 |
| Usage | Indoor |

## Power Supply

### It shall be possible to connect up to 32 power supplies to the system.

### The power supply shall:

#### Provide 2 independent power ports with fixed 28 VDC regulated output.

#### Provide 150 W for battery charging and system power.

#### Provide controlled 500 mA, 24 VDC nominal auxiliary output.

#### Provide color-coded terminal for easy installation.

#### Provide 2 dry relay contacts for AC and DC trouble signaling.

#### Provide yellow and green LEDs and signal outputs to indicate AC, battery and bus communication status.

### Electrical:

|  |  |
| --- | --- |
| Maximum operating voltage in VAC | 230 (-15%, +10%) |
| Minimum AC line frequency in Hz | 47 |
| Maximum AC line frequency in Hz | 63 |
| Minimum output voltage in VDC | 16 |
| Maximum output voltage in VDC | 30 |
| Minimum current consumption in mA | 1070 at rated load and 230 VAC |
| Maximum current consumption in mA | 100 at no-load and 24 VDC |
| **Battery** |  |
| Battery configuration in VDC | 12 |
| Battery type | Lead battery, maintenance-free |
| Minimum ampere hour rating in Ah | 18 |
| Maximum ampere hour rating in Ah | 80 |
| Battery charge voltage in VDC | 27.6 (with thermal compensation) |
| Nominal battery charger output in A | 4.85 |
| Maximum battery charger output in A | 5 |
| **Outputs** |  |
| Maximum sum of output (field-accessible or user-accessible) power in W | ≤ 109 |
| Maximum ripple of all voltage outputs in mV | ≤ 250 |
| **A and B output** |  |
| Type | Supervised, independently short-circuit protected |
| Minimum output voltage in VDC | 26 |
| Maximum output voltage in VDC | 30 |
| Rated voltage in VDC | 28 ± 1 |
| Rated current in mA (A or B) | 2000 |
| Rated current in mA (sum of A and B) | 3000 |
| **Switched auxiliary output** |  |
| Type | Supervised |
| Minimum output voltage in VDC | 24 |
| Maximum output voltage in VDC | 30 |
| Rated voltage in VDC | 24 |
| Rated current in mA | 500 |
| **Panel output** |  |
| Type | Unsupervised |
| Maximum output voltage in VDC | 27.6 |
| Rated voltage in VDC | 24 |
| Rated current in mA | 500 |
| **Trouble output dry contacts** |  |
| Maximum operating voltage in VDC | 30 |
| Rated current in mA | 1000 |

### Mechanical:

|  |  |
| --- | --- |
| Dimensions in cm (H x W x D) | 11.43 x 22.23 x 6.67 |
| Weight in g | 590 |
| Indicators | Green LEDs indicate:   * AC good * Operation monitor   2 x yellow LEDs indicate:   * BAT 1/2 (on = missing battery, blinking = low battery) |
| **Number of inputs** |  |
| Tamper switch input | 1 |
| Thermal compensation circuit | 1 |

### Environmental:

|  |  |
| --- | --- |
| Minimum operating temperature in °C | -10 |
| Maximum operating temperature in °C | 50 |
| Minimum storage temperature in °C | -20 |
| Maximum storage temperature in °C | 60 |
| Minimum temperature compensation (Trim) in °C | -10 |
| Maximum temperature compensation (Trim) in °C | 55 |
| Minimum relative humidity in % | 5 (non-condensing) |
| Maximum relative humidity in % | 95 (non-condensing) |
| Protection class | IP30 IP31 (built into the panel enclosure with an edge protection profile) |
| Security level | IK04  IK06 (built into the panel enclosure with an edge protection profile) |
| Environmental Class | II:  EN50130‑5, VdS 2110 |
| Design type as per EN 50131 | A |
| Usage | Indoor |

## Manufactured units

### The intrusion alarm system shall be a Bosch MAP 5000.

#### The remote programming software shall be Bosch RPS.

#### The open, IP based interface shall be the Open Intrusion Interface (OII).

### The control panel shall be a MAP 5000 Main Panel.

### The keypad shall be a Bosch MAP Control Center.

### The point bus extension module shall be a Bosch MAP LSN Gateway Module.

#### The addressable point bus network shall be Bosch Local Security Network (LSN)

### The interface module shall be a Bosch MAP DE Module.

### The optional CAN Bus splitter module shall be a Bosch MAP CAN Splitter Module.

### The optional expansion module shall be a Bosch ISP-EMIL-120 Expansion Module.

### The optional arming device shall be a Bosch SE xxx LSNi SmartKey Arming Device.

### The panel enclosure shall be a Bosch MAP Panel Enclosure Kit.

### The power enclosure shall be a Bosch MAP Power Enclosure Kit.

### The expansion enclosure shall be a Bosch MAP Expansion Enclosure Kit.

### The Power Supply shall be a Bosch MAP Power Supply 150 W.

### [Remove above article if this is to be a performance-based specification.]

# **EXECUTION**

## Installation

### The installation shall be executed in accordance with manufacturer’s instructions in documentation.

### The installation shall be executed by qualified and certified installers.

### Testing and configuration shall be done in accordance with instructions provided by the manufacturer.

## Training and Support

### The manufacturer shall provide a professional training and a technical support hotline.

# **Other**

## Attachments (optional)

## Further applicable documents (optional)

## List of abbreviations (optional)

## Revision History

|  |  |  |  |
| --- | --- | --- | --- |
| **Issue** | **Date** | **Editor** | **Description of amendment** |
|  |  |  |  |
|  |  |  |  |
|  |  |  |  |

|  |  |
| --- | --- |
| Disclaimer | This document has been prepared for Bosch Security customers and is for information purposes only. All assessments, analysis, recommendations or conclusions contained herein are strictly limited to the products manufactured by Bosch Security and do not subject Bosch Security to any liability. This Report is not intended to provide any advice, assistance or recommendation with regards to the integration of Bosch Security products with or in third party products, systems or network environment, and Bosch Security further declines any liability in relation thereto**.**  THE INFORMATION IN THIS DOCUMENT IS SUBJECT TO CHANGE WITHOUT NOTICE. Bosch Security ASSUMES NO RESPONSIBILITY FOR INACCURACIES OR OMISSIONS AND SPECIFICALLY DISCLAIMS ANY LIABILITIES, LOSSES, OR RISKS, PERSONAL OR OTHERWISE, INCURRED AS A CONSEQUENCE, DIRECTLY OR INDIRECTLY, OF THE USE OR APPLICATION OF ANY OF THE CONTENTS OF THIS DOCUMENT. FOR THE LATEST DOCUMENTATION, CONTACT YOUR LOCAL SUPPLIER OR VISIT US ONLINE AT http://www.boschsecurity.com.  This publication may contain examples of screen captures and reports used in daily operations. |
| Trademarks and patents | Bosch Security and the Bosch Security monogram are registered trademarks of Bosch Security product and logo are registered trademarks of Bosch Security.  Other trade names used in this document may be trademarks or registered trademarks of the manufacturers or vendors of the respective products. |
|  |  |